Technical compliance report (TCR) and guidelines

# Objective of the TCR (and guidelines)

Western Power has prepared this technical compliance report (TCR) with guidelines to assist applicants and Users to report Technical Rules compliance (or variations in compliance) with the Technical Rules (Rules) in relation to connections to the Western Power Network (WPN) within the South West Interconnected Network (SWIN).

# Technical compliance

The Rules are created under chapter 12 of the Electricity Networks Access Code 2004 (Code). They apply as approved and published by the Economic Regulation Authority (Authority). The Rules exist in order to ensure that the objectives of the Code are achieved, and that Western Power’s network safety, reliability and security of supply obligations are met.

Western Power, and all Users, Customers and Applicants (Users hereafter) are required to comply with the Rules, however as set out in sections 12.33 to 12.39 of the Code, Users may apply to Western Power for variations and exemptions to applicable Rules. There is a separate process and form for this.

# Content of the TCR

Users are encouraged to submit an early version of their TCR (for example, during the Scoping phase of the connection process) to support early assessment of compliance with Technical Rules requirements and to highlight the requirement for any exemptions. This may assist to minimise the risk of unforeseen non-compliance(s) causing project delays.

The final version of a TCR (or an equivalent that also meets the Rules’ Section 4 requirements) must be accompanied by certification from a Chartered Professional Engineer with National Engineering Register (NER) standing that the plant is ready for approval to operate.

The format and content of a ‘compliance report’ is ultimately at the discretion of the User. Required minimum information should include:

- compliance assessment (complies/exemption/not applicable) evidence behind assessment (with details of document /revision, location within the reference document(s) for the reference information (see table)

- if the intention is to seek Rules exemption(s), indicate if these will be permanent or temporary

- delete sections that do not apply and insert any others that apply

- orange guide text should be deleted prior to submission

- in some cases it may be necessary to duplicate entries where there is more than one plant item

This template is in Western Power's suggested format and is offered in good faith. Western Power is not liable for any unintended error or omission. It is the responsibility of Users to use it critically, at their own discretion, to demonstrate that they wholly meet their Technical Rules compliance information reporting obligations; including, but not limited to those of sections 4.1 and 4.2. The TCR compliance template table cannot be used to absolve users of any obligation arising under the Technical Rules and the Code.

This release of the Technical Compliance Report template includes references to National Electricity Rules (NER) chapter 5 clauses nominated in the Australian Energy Market Operator (AEMO) Generator Performance Standards (GPS) (available online) for information only. As such, these references do not state or imply equivalence between Technical Rules and NER requirements, nor would performance be assessed against these clauses.

For meeting on-going compliance requirements, Western Power also notes that:

- guidelines for seeking Technical Rules exemptions and Generators’ compliance monitoring programs (CMPs) are available from Western Power’s web site.

- there are additional Technical Rules which apply on an ongoing basis - the ongoing ‘compliant’ performance of Users equipment is also subject to the requirements in Sections 4 and 5 of the Technical Rules (concerning day to day operations, for example, see cl. 4.1.3, and 5.3.3 in the first instance).

- for the purposes of Technical Rules compliance under clause 1.9.4 (for older installations deemed to comply), note that cl. 1.9.5 requires ongoing assessment for suitability for such connections which are otherwise deemed to comply.

# Lodging a Technical Compliance Report

A TCR may be submitted to Western Power in hard copy, addressed to:

Regulatory Compliance Manager

Western Power

GPO Box L921

Perth  WA  6842

or submitted electronically to:

Email: technical.rules@westernpower.com.au

Cc: 	nominated project Access Consultant (as applicable)

# Checklist prior to TCR submission

- TCR table completed (including connection and site details)

- All applicable clauses addressed,

- TCR submitted to Regulatory Compliance Manager

- Copy(ies) of all supporting documents included, each with authorised/approved with revision control details, and any relevant extracts identified. The TCR cannot be assessed without this information, so providing it upfront (with clear referencing) will minimise clarification delays

- All TCR table entries with appropriate assessment entry, supported by detailed reference location information

- All applicable rules are assessed and supported with completed table entries. Clauses which are not applicable should be marked as (N/A)

# Attachment 1	Technical Compliance Report

The final version of a Technical Compliance Report for particular connection works must be accompanied by certification from a Chartered Professional Engineer with National Professional Engineers’ Register Standing that the plant is ready for commissioning.

Delete all orange guiding text when this form is complete.

Western Power internal compliance team usage: Date of Assessment : Assessed by: Associated DM# TR Request assessment: [nnnnnnn]

Site Name: Site and or project name/number

Type of connection: Type, characteristics, capacity and size of load/generator etc.

Technical Rules sections considered in this assessment (delete others that don’t apply):

Delete sections that do not apply and insert any others that apply. In some cases it may be necessary to duplicate entries where there is more than one plant item.

3.2 	REQUIREMENTS FOR ALL USERS

3.3 	REQUIREMENTS FOR CONNECTION OF GENERATING UNITS

3.4 	REQUIREMENTS FOR THE CONNECTION OF LOADS

3.5 	USER’S PROTECTION REQUIREMENTS

3.6	REQUIREMENTS FOR CONNECTION OF SMALL GENERATING UNITS TO THE DISTRIBUTION NETWORK

4.2	COMMISSIONING OF USER'S EQUIPMENT

ATTACHMENT 3 - SUMMARY OF SCHEDULES OF TECHNICAL DETAILS TO SUPPORT APPLICATION FOR CONNECTION

ATTACHMENT 5 - SUBMISSION REQUIREMENTS FOR ELECTRICAL PLANT PROTECTION

ATTACHMENT 7 - TRANSMISSION SYSTEM AND EQUIPMENT TECHNICAL DATA OF EQUIPMENT AT OR NEAR CONNECTION POINT

ATTACHMENT 8 - TRANSMISSION SYSTEM EQUIPMENT AND APPARATUS SETTING DATA

ATTACHMENT 9 - LOAD CHARACTERISTICS AT CONNECTION POINT

- Section: 3. TECHNICAL REQUIREMENTS OF USER FACILITIES

| Clause |  | Sub-clause, or referred cl. | Requirement |  | Compliance | Detailed description |  | Reference information |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  | Document(s) |  | Document date/revision | Detail location within the reference document(s) |  |  |  |  |  |  |
| Delete this row when the form is complete |  |  |  |  | State: COMPLIES, EXEMPTION, N/A | Provide specific detailed descriptions and values |  | Compliance evidentiary document(s) |  | Document date/revision number | Enter the page no., para no., sentence no. etc. |  |  |  |  |  |  |
| 1, 2 |  | As required | Insert relevant clauses and details |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | For example, equipment and details for which cl. 1.9.4 applies. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | Insert rows to enter additional details |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.2 |  |  | REQUIREMENTS FOR ALL USERS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.2.1 |  | Power System Performance Standards | Applies Particularly to Auxiliary Supplies taken from the Grid |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.2.1 |  | (a) | Be capable of operation with South West Interconnected System (SWIS) transmission system parameters varying within the ranges set out in section 2.2. [Frequency 50Hz with variations as Table 2.1 of Rules, Voltage 132kV +/-10% with step changes +/-4.0%, flicker planning levels for HV within Table 2.3 (equivalent to AS/NZS 61000.3.7 Table 2), harmonics limits as Table 2.5 with THD less than 3%, negative phase seq voltage limit 1%, EMI limits as per AS 2344, temporary overvoltage limit as Figure 2.2, rotor angle oscillations damped and stable, and voltages stable in the short term and stably controllable in the long term]. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Note: | The overvoltage envelope specified in Figure 2.1 provides for the level of transient overvoltage excursions expected on the periphery of the transmission and distribution system. Users proposing to connect equipment that is intolerant of high connection point voltage may request the Network Service Provider to undertake a study to determine the maximum potential overvoltage at the proposed connection point. The cost of such a study will be the responsibility of the User requesting it. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.2.1 |  | (b) Flicker (Corresponding NER clause S5.2.5.2 and S5.2.5.6) | User contributions to flicker at the connection point are to be below the limits allocated by the NSP in accordance with AS/NZS 61000.3.7. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.2.1 |  | (c) Harmonics (Corresponding NER clause S5.2.5.2 and S5.2.5.6) | User harmonic emissions at the connection point are to be below the limits allocated by the NSP in accordance with 2.3.4(a) and must not cause exceedances of the levels set out in Tables 2.4 and 2.5. User equipment shall not inject DC. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.2.1 |  | (d) Negative phase sequence voltage (Corresponding NER clause S5.2.5.2 and S5.2.5.6) | (1) A User connected to all three phases must balance the current drawn in each phase at its connection point so as to achieve 10-minute average levels of negative sequence voltage at the connection point that are equal to or less than the values set out in Table 2.6. (2) A User directly connected to the transmission system must be connected to all three phases. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.2.1 |  | (e) Electromagnetic Interference | The user shall ensure that EMI caused by its equipment does not exceed the limits set out in Tables 1 and 2 of AS 2344. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.2.1 |  | (f) Fault levels (1), (2) and (3) | Fault capacity at connection point voltage is to comply with the connection agreement. As applicable in parts (1), (2) and (3)… |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.2.2 |  | Main Switch | A User must be able to de-energise its own equipment without reliance on the NSP. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.2.3 |  | User Power Quality Monitoring | The NSP may require a user to provide for NSP power quality monitoring and recording equipment |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.2.4 |  | Power system simulation studies | A user must provide to the NSP a defined range of information to facilitate power system simulation studies. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.2.5 |  | Technical Matters to be Coordinated | A User and the NSP must agree upon these matters |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.2.5 |  | (a) | Design at the connection point |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.2.5 |  | (b) | Protection |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.2.5 |  | (c) | Control characteristics |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.2.5 |  | (d) | Communications, remote controls, indications and alarms |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.2.5 |  | (e) | Insulation Co-ordination and lightning protection |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.2.5 |  | (f) (Corresponding NER clause S5.2.8) | Fault levels and total clearance times |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.2.5 |  | (g) | Switching and isolation facilities |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.2.5 |  | (h) | Interlocking arrangements |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.2.5 |  | (i) | Synchronising facilities |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.2.5 |  | (j) | Provision of Information |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.2.5 |  | (k) | Computer model and power system simulation study requirements |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.2.5 |  | (l) | Load shedding and islanding schemes |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.2.5 |  | (m) | Any special test requirements |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3 |  |  | REQUIREMENTS FOR CONNECTION OF GENERATING UNITS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.1 |  | (a) | General requirement to comply with section 3.3 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.1 |  | (b) | A generator must comply with directions. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.1 |  | (c) | This clause applies to generators > 10 MW |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.1 |  | (d) (Corresponding NER clause S5.2.5.12) | A generating unit must have characteristics and controls sufficient not to cause any reduction of power transfer capability because of (1) reduced rotor angle stability (2) reduced frequency stability, or (3) reduced voltage stability, that would apply if the generating unit were not connected. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.1 |  | (e) | An unplanned trip of a generating unit must not cause an increased need for load shedding over and above that would apply if the generating unit were not connected. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.1 |  | (f) | A generator must ensure that its transients do not adversely affect the NSP and other users. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.1 |  | (g) | Unless otherwise specified in these Rules, the technical requirements for generating units apply at the connection point. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.1 |  | (h) | A generating unit must disconnect from the distribution system if the distribution feeder to which it is connected is separated from the remainder of the power system. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.2 |  | Provision of Information | The User must provide all data required by the NSP to assess the impact of a generating unit on the performance and security of the transmission and distribution system. Details of the kinds of data that may be required are included in Attachments 3, 4 and 5 [of the Technical Rules]. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.3 |  | Detailed Technical Requirements Requiring Ongoing Verification | A Generator must verify compliance of its own equipment with the technical requirements described of this clause 3.3.3 by the methods described in clause 4.1.3 [of these Rules]. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.3.1 |  | (a) (Corresponding NER clause S5.2.5.1) | Each generating unit, and the power station in which the generating unit is located, must be capable of continuously providing its full reactive power output within the full range of steady state voltages at the connection point permitted under clause 2.2.2. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.3.1 |  | (b) (Corresponding NER clause S5.2.5.1) | Each generating unit must include a controller that is capable of varying the reactive power at the connection point between the maximum import level and maximum export level required by this clause 3.3.3.1. This control must be continuous to the extent that it must not depend on mechanically switched devices other than an on-load tap changer forming part of the generating unit transformer. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.3.1 |  | (c) (Corresponding NER clause S5.2.5.1) | (1) Each synchronous generating unit, while operating at any level of active power output between its registered maximum and minimum active power output level, must be capable of (A) supplying at its generator machine's terminals an amount of reactive power of at least the amount equal to the product of the rated active power output of the generating unit at nominal voltage and 0.750; and (B) absorbing at its generator machine's terminals an amount of reactive power of at least the amount equal to the product of the rated active power output of the generating unit at nominal voltage and 0.484. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.3.1 |  | (d) – (h) (Corresponding NER clause S5.2.5.1) | <<Insert rows from Technical Rules clauses with details as they apply>> |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.3.2 |  | Generating Unit Performance Standard | A synchronous generating unit or an induction generating unit must be designed to generate a constant voltage level with balanced phase voltages and harmonic voltage distortion equal to or less than permitted in accordance with either Australian Standard AS 1359 "General Requirements for Rotating Electrical Machines" or a recognised equivalent international standard as agreed between the NSP and the User if the generating unit was not connected to the transmission or distribution system. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.3.3 |  | Generating Unit Response To Disturbances In The Power System | See specific requirements below |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.3.3 |  | (a) Overview | The following are design requirements for generating units and their auxiliary systems for continuous uninterrupted operation while being subjected to off-nominal frequency and voltage excursions. Continuous uninterrupted operation is defined in clause 3.3.3.3(h). |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.3.3 |  | (b) Immunity to Frequency Excursions. (Corresponding NER clause S5.2.5.3) | A generating unit, and a power station in which the generating unit is located, must be capable of continuous uninterrupted operation within the power system frequency envelope specified in Figure 3.4. Operation for a period of at least 10 seconds is required each time the frequency is below 47.5 Hz. Operation for a period of at least 6 seconds is required each time the frequency is above 52 Hz. Below 47Hz, and above 52.5 Hz instantaneous disconnection of generating units is permitted. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.3.3 |  | (c) Immunity to Voltage Excursions (Corresponding NER clause S5.2.5.4) | (1) A generating unit, and the power station in which the generating unit is located, must be capable of continuous uninterrupted operation transmission or distribution system faults which cause the voltage at the connection point to drop below the nominal voltage for a period equal to the circuit breaker failure fault clearing time to clear the fault plus a safety margin of 30 msec, followed by a period of 10 seconds where the voltage may vary in the range 80% to 110% of the nominal voltage, and a subsequent return of the voltage within the range 90 to 110% of the nominal voltage. (2) Notwithstanding the requirements of clause 3.3.3.3(c)(1) no generating unit shall be required to be capable of continuous uninterrupted operation where the voltage at the connection point falls outside the envelope shown in Figure 3.5. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.3.3 |  | (d) Immunity to Rate-of-Change-of-Frequency (Corresponding NER clause S5.2.5.3) | A generating unit, and the power station in which the generating unit is located, must be capable of continuous uninterrupted operation for the rate-of-change-of frequency of up to 4 Hz per second. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.3.3 |  | (e) Immunity to High Speed Auto Reclosing | A generating unit, and the power station in which the generating unit is located, must be capable of continuous uninterrupted operation for voltage transients caused by high speed auto-reclosing of transmission lines irrespective of whether or not a fault is cleared during a reclosing sequence. See Figure 3.6 for details of the low voltage ride through requirement during auto-reclose operation. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.3.3 |  | (f) Post-Fault Reactive Power of a Power Station with Non-Synchronous Generating Units (Corresponding NER clause S5.2.5.5) | After fault clearing, the power station in which a non-synchronous generating unit is located must not absorb reactive power from the transmission system or the distribution system. Any pre-fault absorption of reactive power has to be terminated within 200 ms after clearing of the fault. The absorption is permitted to recommence, if required by the applicable voltage control strategy, after the post-fault voltages stabilize for at least 60 seconds at an above nominal value. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.3.3 |  | (g) Post Fault Voltage Control of a Connection Point (Corresponding NER clause S5.2.5.5) | Each generating unit must be fitted with a governor and a voltage regulator so that, following the occurrence of any credible contingency event and changed power system conditions after disconnection of the faulted element, the generating unit must be capable of delivering to the transmission or distribution system active power and reactive power sufficient to ensure that the connection point voltage is within the range for continuous uninterrupted operation for that generating unit. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.3.3 |  | (h) Continuous Uninterrupted Operation (Corresponding NER clause S5.2.5.5) | For the purpose of this clause 3.3.3.3, a generating unit is considered to remain in continuous uninterrupted operation if: (1) the generating unit is not disconnected from the transmission or distribution system due to protection system operation; (2) the active power output returns to the generating unit's pre-fault electric power output within 200 milliseconds after the voltage has returned to between 80% to 110% of nominal voltage. In making this assessment allowances may be made for: (A) any variation in active power output for non-synchronous generating units due to variation in the primary source of energy (B) any variation in active power output of synchronous generating units due to any reduction in the power system frequency in accordance with the registered capability of the generating unit. (3) the reactive power control mode in which the generating unit was operating prior to the credible contingency event occurring does not change, unless required by clause 3.3.3.3(f). |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.3.4 |  | Sudden Reduction in Active Power Requirement (Corresponding NER clause S5.2.5.7) | A generating unit must be capable of continuous uninterrupted operation, as defined in clause 3.3.3.3(h) during and following a sudden reduction in required active power generation imposed from the power system, provided that the reduction is less than 30% of the generator machine's nameplate rating and the required active power generation remains above the generating unit's registered minimum active power generation capability. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.3.5 |  | Ramping Rates (a) (Corresponding NER clause S5.2.5.14) | (a) A scheduled generating unit, in a thermally stable state, must be capable of increasing or decreasing active power generation in response to a manually or remotely initiated loading order to change the level of generated active power at a rate not less than 5% of the generator machine's nameplate rating per minute. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.3.5 |  | Ramping Rates (b) (Corresponding NER clause S5.2.5.14) | (b) A power station that is not subject to dispatch by System Management must not increase or decrease its active power generation at a rate greater than 10MW per minute or 15% of the power station’s aggregate nameplate rating per minute, whichever is the greater, except when more rapid changes are necessary due to the strength of the energy source moving outside the power station’s design range. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.3.6 |  | Safe Shutdown Without External Electricity Supply | A generating unit must be capable of being safely shut down without an electricity supply being available from the transmission or distribution system at the relevant connection point. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.3.7 |  | Restart Following Restoration Of External Electricity Supply | (a) A generating unit must be capable of being restarted and synchronised to the transmission or distribution system without unreasonable delay following restoration of external supply from the transmission or distribution system at the relevant connection point, after being without external supply for 2 hours or less, provided that the generating unit was not disconnected due to an internal fault. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.3.7 |  | (b) | (b) The maximum restart time, agreed by the Generator and the NSP, must be specified in the relevant connection agreement. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.3.8 |  | Protection Of Generating Units From Power System Disturbances (Corresponding NER clause S5.2.5.8) | See below |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.3.8 |  | (a) (Corresponding NER clause S5.2.5.8 and S5.2.5.10) | A generating unit may be disconnected automatically from the transmission or distribution system in response to abnormal conditions arising from the behaviour of the power system. However a generating unit must not be disconnected if the power system conditions at the connection point remain within the envelope described in clause 3.3.3.3 for continuous uninterrupted operation. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.3.8 |  | (b) (Corresponding NER clause S5.2.5.8 and S5.2.5.10) | The abnormal conditions referred to in clause 3.3.3.8(a) include: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | (1) loss of synchronism; |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | (2) high or low frequency outside the generator off-nominal frequency operation capability requirements specified in Figure 3.4; |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | (3) sustained excessive generating unit stator current that cannot be automatically controlled; |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | (4) high or low stator voltage outside the generator machine rating; |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | (5) voltage to frequency ratio outside generator machine rating; |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | (6) negative phase sequence current outside the generator machine rating; and |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | (7) any similar condition agreed between the Generator and the NSP after consultation with System Management. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.3.8 |  | (c) (Corresponding NER clause S5.2.5.8 and S5.2.5.10) | The actual design and settings of the protection equipment installed in order to disconnect a generating unit in accordance with clause 3.3.3.8(a) must be consistent with power system performance requirements specified in Section 2 and must be approved by the NSP. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.3.9 |  | Generating Unit Transformer | See below |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.3.9 |  | (a) Transformer Impedance | The maximum permitted impedance of a generating transformer is 20% of the generator's MVA rating |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.3.9 |  | (b) Vector Group | A generating unit transformer's vector group must be agreed with the NSP. The vector group must be compatible with the power system at the connection point and preference may be given to vector groups with a zero sequence opening between high voltage and low voltage windings. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.3.9 |  | (c) Tap Changing | A generating unit transformer of a generating unit or wind farm must be capable of on-load tap-changing within the range specified in the connection agreement. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.3.10 |  | De-energisation of Generator Circuits | The NSP's relevant circuit breaker may be used as a point of de-energisation, instead of the main switch specified in clause 3.2.2 provided that the Generator meets the following requirements: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.3.10 |  | (a) | The Generator must be able to synchronise any parallel generating equipment to the transmission or distribution system across a circuit breaker owned by the Generator, |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.3.10 |  | (b) | The Generator must be able to clear a fault on its equipment: (1) without adversely affecting any other User or potential User; and (2) within the fault clearance times specified in clause 3.5.2(b); provided that the substation where the NSP's relevant circuit breaker is located is in its normal operating configuration |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | if: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.3.10 |  | (c) | (1) the Generator has only one circuit at the connection point; and (2) the NSP's relevant circuit breaker is located in a meshed substation, and if … (3) and (4), then the Generator may de-energise its equipment by sending a trip signal to the NSP's relevant circuit breaker. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.3.10 |  | (d) | the Generator must own a visible point of isolation between the NSP's relevant circuit breaker and the Generator's equipment for each piece of equipment connected to the transmission or distribution system. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.4 |  | Monitoring and Control Requirements See sub-items below |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.4.1 |  | Remote Monitoring (Corresponding NER clause S5.2.6.1) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.4.1 |  | (a) (Corresponding NER clause S5.2.6.1) | The NSP will require the User to: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | (a) (1) | provide remote monitoring equipment ("RME") to enable the NSP or System Management to monitor performance of a generating unit (including its dynamic performance) where this is reasonably necessary in real time for control, planning or security of the power system; and |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | (a) (2) | upgrade, modify or replace any RME already installed in a power station provided that the existing RME is, in the opinion of the NSP, no longer fit for purpose and notice is given in writing to the relevant Generator accordingly. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.4.1 |  | (b) (Corresponding NER clause S5.2.6.1) | Any RME provided, upgraded, modified or replaced (as applicable) must conform to an acceptable standard as agreed by the NSP and must be compatible with the NSP’s and System Management's SCADA system. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.4.1 |  | (c) (Corresponding NER clause S5.2.6.1) | Input information to RME may include the following: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | (c) (1) | Status Indications |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | (A) generating unit circuit breaker open/closed (dual point) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | (B) remote generation load control on/off |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | (C) generating unit operating mode |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | (D) turbine control limiting operation, and |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | (E) connection to the transmission or distribution system |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | (c) (2) | Alarms |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | (A) generating unit circuit breaker/main switch tripped by protection |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | (B) prepare to off load, and |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | (C) protection defective alarms |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | (c) (3) | Measured Values |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | (A) transmission system |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | (i) Gross active power output of each generating unit |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | (ii) Gross reactive power output of each generating unit |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | (iii) Net station active power import or export at each connection point |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | (iv) Net station reactive power import or export at each connection point |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | (v) Generating unit stator voltage |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | (vi) Generating unit transformer tap position |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | (vii) Net station output of active energy (impulse) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | (viii) Generating unit remote generation control high limit value |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | (ix) Generating unit remote generation control low limit value |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | (x) Generating unit remote generation control rate limit value |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | (B) Distribution System |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | - Main switch active power import or export |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | - Main switch reactive power import or export |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | - Voltage on the NSP side of main switch |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | (c) (4) | Such other input information reasonably required by the NSP. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.4.2 |  | Remote Control |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.4.2 |  | (a) | The NSP or System Management may, for any generating unit which may be unattended when connected to the transmission or distribution system, require the Generator to: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | (1) provide remote control equipment to enable the NSP or System Management to disconnect a generating unit from the transmission or distribution system; and |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | (2) upgrade, modify or replace any RCE already installed in a power station provided that the existing RCE is, in the opinion of the NSP or System Management, no longer fit for purpose and notice is given in writing to the relevant User accordingly. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.4.2 |  | (b) | Any RCE provided, upgraded, modified or replaced (as applicable) under clause 3.3.4.2(a) must conform to an acceptable standard as agreed by the NSP and must be compatible with the NSP's SCADA system, including the requirements of clause 5.11. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.4.3 |  | Communications Equipment (Corresponding NER clause S5.2.6.2) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.4.3 |  | (a) (Corresponding NER clause S5.2.6.2) | A Generator must provide communications paths (with appropriate redundancy) between the RME and RCE installed at any of its generating units to a communications interface at the relevant power station and in a location reasonably acceptable to the NSP. ..... Communications systems between this communications interface and the relevant control centre are the responsibility of the NSP unless otherwise agreed. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.4.3 |  | (b) (Corresponding NER clause S5.2.6.2) | Telecommunications between the NSP and Generators must be established in accordance with the requirements set down below for operational communications. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.4.3 |  | (c) (Corresponding NER clause S5.2.6.2) | Primary Speech Communications Channel |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | (c) (1) | A Generator must provide and maintain a speech communication channel by means of which routine and emergency control telephone calls may be established between the Generator's responsible engineer or operator and System Management or the NSP, whichever is applicable. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | (c) (2) | The speech communication channel provided must meet the requirements of the NSP and System Management. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | (c) (3) | Where the public switched telephone network is to be used as the primary speech communication channel, a sole-purpose connection, which must be used only for operational communications, shall be provided. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.4.3 |  | (d) (Corresponding NER clause S5.2.6.2) | Back-up Speech Communications Channel |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | (d) (1) | The NSP must provide a separate telephone link or other backup speech communications channel for the primary speech communications channel. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | (d) (2) | The Network Service Provider must be responsible for planning installing and maintaining the back-up speech communications channel, and for obtaining radio licenses if required. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | (d) (3) | The Network Service Provider may recover the cost of providing the backup speech communications channel from the generator as agreed in the relevant connection agreement. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.4.4 |  | Frequency Control (Corresponding NER clause S5.2.5.11) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.4.4 |  | (a) (Corresponding NER clause S5.2.5.11) | All generating units must have an automatic variable speed control characteristic. Turbine control systems must include facilities for both speed and load control. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.4.4 |  | (b) (Corresponding NER clause S5.2.5.11) | Generating units must be capable of operation in a mode in which they will automatically and accurately alter active power output (every four seconds) to allow for changes in associated loads and for change s in frequency of the transmission and distribution system and in a manner to sustain high initial response. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.4.4 |  | (c) (Corresponding NER clause S5.2.5.11) | A Generator must, operate a generating unit in the mode specified in A Generator must, operate a generating unit in the mode specified in clause 3.3.4.4(b) unless instructed otherwise by System Management or the Network Service Provider, as the case requires. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.4.4 |  | (d) Dead Band (Corresponding NER clause S5.2.5.11) | The dead band of a generating unit (the sum of increase and decrease in power system frequency before a measurable change in the generating unit 's active power output occurs) must be less than 0.05 Hz. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.4.4 |  | (e) Control Range (Corresponding NER clause S5.2.5.11) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | (e) (1) | For dispatchable generating units: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | (A) The overall response of a dispatchable generating unit for power system frequency excursions must be settable and be capable of achieving an increase in the generating unit 's active power output of not less than 5% for a 0.1 Hz reduction in power system frequency (4% droop) for any initial output up to 85% of rated output. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | (B) A dispatchable generating unit must also be capable of achieving a reduction in the generating unit 's active power output of not less than 5% for a 0.1 Hz increase in system frequency provided this does not require operation below the technical minimum. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | (C) For initial outputs above 85% of rated active power output, a generating unit’s response capability must be included in the relevant connection agreement, and the Generator must ensure that the generating unit responds in accordance with that connection agreement. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | (D) Thermal generating units must be able to sustain load change s of at least 10% for a frequency decrease and 30% for a frequency increase if change s occur within the above limits of output |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | (e) (2) | For non- dispatchable generating units, a generating unit must be capable of achieving a reduction the generating unit’s active power output for an increase in system frequency, provided the latter does not require operation below technical minimum. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.4.4 |  | (f) Rate of Response (Corresponding NER clause S5.2.5.11) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | (f) (1) | For dispatchable generating units , for any frequency disturbance, a scheduled generating unit must achieve at least 90% of the maximum response expected according to the droop characteristic within 6 seconds for thermal generating units or 30 seconds for hydro generating units and the new output must be sustained for not less than a further 10 seconds. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | (f) (2) | For non-dispatchable generating units, for any frequency disturbance, a generating unit must achieve at least 90% of the maximum response expected within 2 seconds and the new output must be sustained for not less than a further 10 seconds. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.4.5 |  | Voltage Control System (Corresponding NER clause S5.2.5.13) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.4.5 |  | (a) (Corresponding NER clause S5.2.5.13) | The excitation control system of a synchronous generating unit must be capable of: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | (a) (1) | limiting the reactive power absorbed or supplied by the generating unit to within generating unit’s capability for continuous operation given its load level; |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | (a) (2) | controlling the generating unit’s excitation to maintain the short time average generating unit stator voltage below its highest rated level (which must be at least 5% above the nominal stator voltage ); |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | (a) (3) | maintaining adequate generating unit stability under all operating conditions and providing power system stabilising action if fitted with a power system stabiliser; |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | (a) (4) | providing a 5 second ceiling excitation voltage of at least twice the excitation voltage required to achieve maximum continuous reactive power rating at nominal voltage and at nominal active power output; |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | (a) (5) | providing reactive current compensation settable for droop or remote point voltage control. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.4.5 |  | (b) (Corresponding NER clause S5.2.5.13) | Synchronous generating units must be fitted with fast acting excitation control systems in accordance with good electricity industry practice |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.4.5 |  | (c) (Corresponding NER clause S5.2.5.13) | New non-synchronous generating units must be fitted with fast acting voltage and / or reactive power control systems in accordance with good electricity industry practice, which must be approved by the Network Service Provider. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.4.5 |  | (d) (Corresponding NER clause S5.2.5.13) | Synchronous generating units with ratings in excess of 30 MW or smaller generating units within a power station with a total active power output capability in excess of 30 MW must incorporate power system stabiliser (PSS) circuits which modulate the generating unit field voltage in response to change s in power output and/or shaft speed and/or any other equivalent input signal approved by the Network Service Provider . The stabilising circuits must be responsive and adjustable over a frequency range which must include frequencies from 0.1 Hz to 2.5 Hz. Power system stabiliser circuits may be required on synchronous generating units with ratings less than or equal to 30 MW or smaller synchronous generating units within a power station with a total active power output capability less than or equal to 30 MW if power system simulations indicate a need for such a requirement. Before commissioning of any power system stabiliser, the Generator must propose preliminary settings for the power system stabiliser, which must be approved by the Network Service Provider. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.4.5 |  | (e) (Corresponding NER clause S5.2.5.13) | Power system stabilisers may also be required for non-synchronous generating units . The performance characteristics of these generating units with respect to power system stability must be similar to those required for synchronous generating units . The requirement for a power system stabiliser and its structure and settings will be determined by the Network Service Provider from power system simulations. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.4.5 |  | (f) (Corresponding NER clause S5.2.5.13) | The performance characteristics required for AC exciter, rotating rectifier and static excitation system s are specified in Table 3.1: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | (f) Table 3.1, Row 1 | Synchronous generator excitation control system performance requirements Performance Item = Sensitivity: A sustained 0.5% error between the voltage reference and the sensed voltage must produce an excitation voltage change of not less than 1.0 per unit. Minimum open loop gain: For Static Excitation, AC Exciter or Rotating Rectifier, Ratio = 200. Note 1 applies. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | (f) Table 3.1, Row 2 | Synchronous generator excitation control system performance requirements Performance Item = Field voltage rise time: Time for field voltage to rise from rated voltage to excitation ceiling voltage following the application of a short duration impulse to the voltage reference: For Static Excitation 0.05 seconds maximum, For AC Exciter or Rotating Amplifier 0.5 seconds maximum. Notes 2 and 4 apply. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | (f) Table 3.1, Row 3 | Synchronous generator excitation control system performance requirements Performance Item = Settling time, Settling time with the generating unit unsynchronised following a disturbance equivalent to a 5% step change in the sensed generating unit terminal voltage. For Static Excitation 1.5 seconds maximum, For AC Exciter or Rotating Amplifier 2.5 seconds maximum. Note 3 applies. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | (f) Table 3.1, Row 4 | Synchronous generator excitation control system performance requirements Performance Item = Settling time, Settling time with the generating unit synchronised following a disturbance equivalent to a 5% step change in the sensed generating unit terminal voltage. Must be met at all operating points within the generating unit capability. For Static Excitation 2.5 seconds maximum, For AC Exciter or Rotating Amplifier 5 seconds maximum. Note 3 applies. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | (f) Table 3.1, Row 5 | Synchronous generator excitation control system performance requirements Performance Item = Settling time, Settling time following any disturbance which causes an excitation limiter to operate. For Static Excitation 5 seconds maximum, For AC Exciter or Rotating Amplifier 5 seconds maximum. Note 3 applies. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | (f) Table 3.1 Notes | Note 1: One per unit excitation voltage is that field voltage required to produce nominal voltage on the air gap line of the generating unit open circuit characteristic (Refer IEEE Standard 115-1983 -Test Procedures for Synchronous Machines). Excitation control system with both proportional and integral actions must achieve a minimum equivalent gain of 200. Note 2: Rated field voltage is that voltage required to give nominal generating unit terminal voltage when the generating unit is operating at its maximum continuous rating. Rise time is defined as the time taken for the field voltage to rise from 10% to 90% of the increment value. Note 3: Settling time is defined as the time taken for the generating unit terminal voltage to settle and stay within an error band of ±10% of its increment value. Note 4: Field voltage means generating unit field voltage. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.4.5 |  | (g) (Corresponding NER clause S5.2.5.13) | The performance characteristics required for the voltage or reactive power control systems of all non-synchronous generating units are specified in Table 3.2: Table 3.2 Non-synchronous generator voltage or reactive power control system performance requirements |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.4.5 |  | (h) | The structure and parameter settings of all components of the control system , including the voltage regulator, reactive power regulator, power system stabiliser, power amplifiers and all excitation limiters, must be approved by the Network Service Provider . |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.4.5 |  | (i) | The structure and settings of the voltage / excitation control system must not be changed, corrected or adjusted in any manner without the prior written approval of the Network Service Provider. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.4.5 |  | (j) | Control system settings may require alteration from time to time as advised by the Network Service Provider . The preliminary settings backed up by any calculations and system studies to derive these settings must be provided by the Network Service Provider at least two months before the system tests stated in clause 4.1.3 are undertaken. A Generator must cooperate with the Network Service Provider by applying the new settings and participating in tests to demonstrate their effectiveness. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.4.5 |  | (k) (Corresponding NER clause S5.2.5.13) | Excitation limiters must be provided for under excitation and over excitation of synchronous generating units and may be provided for voltage to frequency ratio. The generating unit must be capable of stable operation for indefinite periods while under the control of any limiter. Limiters must not detract from the performance of any stabilising circuits and must have settings applied which are coordinated with all protection systems . |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.5 |  | Power Station Auxiliary Transformer s (Corresponding NER clause S5.2.7) | In cases where a power station takes its auxiliary supplies through a transformer by means of a separate connection point , the User must comply with the conditions for connection of loads (refer to clause 3.4) in respect of that connection point . |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.6 |  | Synchronising |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.6 |  | (a) | For a synchronous generating unit the Generator must provide and install manual or automatic synchronising at the generating unit circuit breakers. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.6 |  | (b) | The Generator must provide check synchronising on all generating unit circuit breakers and any other circuit breakers, unless interlocked (as outlined in clause 3.4), that are capable of connecting the User's generating equipment to the transmission or distribution system . |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.6 |  | (c) | Prior to the initial synchronisation of the generating unit(s) to the transmission or distribution transmission system , the Generator and the Network Service Provider must agree on written operational procedures for synchronisation . |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.7 |  | Secure Electricity Supplies | A Generator must provide secure electricity supplies of adequate capacity for the operation of equipment performing metering, communication, monitoring, and protection functions for at least 8 hours after the loss of AC supplies to that equipment . |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.8 |  | Design Requirements For Generator’s Substations | A Generator must comply with the requirements of clause 3.4.8. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.9 |  | Computer Model |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.9 |  | (a) | A Generator must provide a software model of each generating unit suitable for use in the software package which is used by the Network Service Provider at the time of signing the relevant connection agreement . The model must automatically initialise its parameters from load flow simulations. Once a simulation case has been compiled, change s in the load flow such as changes in voltage , generating unit output, voltage set point must not require the study case to be recompiled. It is the preference of the Network Service Provider that the model be made available to the provider for inclusion in the standard software package library. The source code of the model must also be provided. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.9 |  | (b) | Generators must demonstrate to the satisfaction of the Network Service Provider that the model adequately represents the performance of the generating unit over its load range and over the system frequency operating range of clause 2.2.1, Table 2.1. The normal method of model verification is through testing. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.9 |  | (c) | The structure and parameter settings of all components of the turbine and excitation control equipment must be provided to the Network Service Provider in sufficient detail to enable the dynamics of these components to be characterised in the computer model for short and long term simulation studies. This must include a control block diagram in suitable form to perform dynamic simulations and proposed and final parameter settings for the turbine and excitation control system s for all expected modes of turbine control system operation. The final parameter settings must not be varied without prior approval of the Network Service Provider . |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.9 |  | (d) | The applicable structure and parameter settings include: (1) speed/load controller ; (2) key protection and control loops; (3) actuators (for example hydraulic valve positioning systems); and (4) limiters. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.9 |  | (e) | A Generator may connect to the transmission or distribution system without fully complying with the requirements of subclauses (a) to (d) of this clause 3.3.9 provided that the Generator agrees in the relevant connection agreement to alternative arrangements, acceptable to the Network Service Provider , for the provision of a compatible software model of the generating unit should the Network Service Provider upgrade or change its power system simulation software. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.9 |  | (f) | A Generator that was connected to the transmission or distribution system prior to the rules commencement date, and which has not fully complied with the requirements of subclauses (a) to (d) of this clause 3.3.9, must support the computer model for changes in the nominated software for the duration of its connection to the transmission or distribution system . |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.4 |  |  | REQUIREMENTS FOR THE CONNECTION OF LOADS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.4.1 |  | Obligations of Consumers |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.4.1 |  | (a) | A Consumer must ensure that all facilities associated with the relevant connection point at all times comply with the applicable requirements and conditions of connection for loads : (1) as set out in this clause 3.4; and (2) in accordance with any relevant connection agreement with the Network Service Provider. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.4.1 |  | (b) | A Consumer must operate its facilities and equipment in accordance with any and all directions given by System Management or the Network Service Provider under these Rules or under any written law. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.4.2 |  | Overview |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.4.2 |  | (a) | This clause 3.4 applies to the connection of equipment and facilities of Consumers to the transmission and distribution systems . |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.4.2 |  | (b) | The requirements set out in this clause 3.4 generally apply to the connection of a large load to the transmission or distribution network . The specific requirements for the connection of a particular Consumer’s equipment and facilities must be determined by the Network Service Provider and will depend on the magnitude and other characteristics of the Consumer's load , the power transfer capacity, voltage and location of the connection point, and characteristics of the local transmission or distribution system in the vicinity of the connection point . |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.4.2 |  | (c) (Corresponding NER clause S5.2.5.9) | A Consumer must provide equipment capabilities, protection and control systems that ensure that its load : (1) does not cause excessive load fluctuations, reactive power draw or, where applicable, stalling of motor loads that would have an adverse impact on other Users , System Management , the Network Service Provider or the performance of the power system . (2) does not cause any reduction of inter-regional or intra-regional power transfer capability based on: (A) frequency stability, or (B) voltage stability, by more than its loading level whenever connected relative to the level that would apply if the Consumer were disconnected. [This requirement is intended to safeguard from transients caused by relatively large Users with a high proportion of motor loads; for example, to safeguard one mining operation from another.] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.4.3 |  | Power Frequency Variations | A Consumer must ensure that the equipment connected to its connection point is capable of continuous uninterrupted operation (other than when the facility is faulted) if variations in supply frequency of the kind described in clause 2.2.1(c) occur. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.4.4 |  | Power Frequency Voltage Variations | A Consumer must ensure that the equipment connected to its connection point is capable of continuous uninterrupted operation (other than when the facility is faulted) if variations in supply voltage of the kind described in clause 2.2.2. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.4.5 |  | Provision of Information |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.4.5 |  | (a) | Before connection to the transmission or distribution system , a Consumer must provide all data relevant to each connection point that is required by the Network Service Provider in order to complete the detailed design and installation of the relevant connection assets, to ensure that there is sufficient power transfer capability in the transmission and distribution systems to supply the Consumer's load and that connection of the Consumer’s load will not have an adverse impact other Users, or on the performance of the power system. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.4.5 |  | (b) | The specific data that must be provided by a Consumer in respect of a particular connection point will depend on characteristics of the Consumer's loads , the power transfer capacity of the connection point as specified in the relevant connection agreement , the voltage and location of the connection point, and characteristics of the local transmission or distribution system in the vicinity of the connection point . Equipment data that may need to be provided includes: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.4.5 |  | (b) (1) | interface protection details including, line diagram, grading information, secondary injection and trip test certificate on all circuit breakers; |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | (b) (2) | metering system design details for equipment being provided by the Consumer |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | (b) (3) | a general arrangement locating all the major loads on the site; |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | (b) (4) | a general arrangement showing all exits and the position of all electrical equipment in substations that are directly connected to the connection point ; |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | (b) (5) | type test certificates for new switchgear and transformer s, including measurement transformer s to be used for metering purposes; |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | (b) (6) | the proposed methods of earthing cables and other equipment plus a single line earthing diagram; |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | (b) (7) | equipment and earth grid test certificates from approved test authorities; |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | (b) (8) | operational procedures; |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | (b) (9) | details of time-varying, non-sinusoidal and potentially disturbing loads ; |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | (b) (10) | SCADA arrangements; |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | (b) (11) | load details including maximum demand profiles; |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | (b) (12) | a line diagram and service or incoming cable routes and sizes; and |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | (b) (13) | preferred location of the connection point . [Typically, a small domestic Consumer will only be required to provide the data referred to in clauses 3.4.5(b)(12) and clause 3.4.5(b)(13).] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.4.5 |  | (c) | In addition to the requirements in clause 3.4.5(a) and (b), the Consumer must provide load data reasonably required by the Network Service Provider . Details of the kinds of data that may be required are included in Attachment 3 and Attachment 9. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.4.6 |  | Design Standards |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.4.6 |  | (a) | The equipment connected to a Consumer’s connection point must comply with the relevant Australian Standard s as applicable at the time of first installation of the equipment , the Electricity (Supply Standard and System Safety) Regulations 2001 (WA), good electricity industry practice and these Rules and it must be capable of withstanding the power frequency voltages and impulse levels specified by the Network Service Provider. . |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.4.6 |  | (b) | The circuit breakers, fuses and other equipment provided to isolate a Consumer’s facilities from the transmission and distribution system in the event of a fault must be capable of breaking, without damage or restrike, the fault currents specified by the Network Service Provider for the relevant connection point . |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.4.6 |  | (c) | The equipment ratings connected to a Consumer’s connection point must coordinate with the equipment installed on the power system . |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.4.7 |  | Power Factor Requirements |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.4.7 |  | (a) | Power factor ranges to be met by loads connected to the transmission system and those connected to the distribution system and rated 1MVA or more are shown in the Table 3.3. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | Table 3.3 Power factor requirements for loads |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.4.7 |  | (a) Table 3.3 | Permissible Range (Extract for 132kV) Supply Voltage (nominal) = 66kV to 132kV Power factor range (half-hour average, unless otherwise specified by the Network Service Provider) = 0.95 lagging to unity |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.4.7 |  | (b) | The power factor range to be met by loads of less than 1 MVA connected to the distribution system is 0.8 lagging to 0.8 leading. Where necessary to ensure the satisfactory operation of the distribution system , a different power factor range may be specified in the relevant connection agreement . |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.4.7 |  | (c) | The Network Service Provider may permit a lower lagging or leading power factor where this will not reduce system security and/or quality of supply , or require a higher lagging or leading power factor to achieve the power transfer s required by the load. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.4.7 |  | (d) | A shunt capacitor installed to comply with power factor requirements must comply with the Network Service Provider's requirements to ensure that the design does not severely attenuate audio frequency signals used for load control or operations. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.4.7 |  | (e) | A static VAr compensator system installed for either power factor or quality of supply requirements must have a control system that does not interfere with other control functions on the electricity transmission and distribution system . Adequate filtering facilities must be provided if necessary to absorb any excessive harmonic currents. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.4.8 |  | Design Requirements for Consumers ' Substations | Equipment in or for any Consumer’s substation that is connected directly to a connection point must comply with the following requirements: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.4.8 |  | (a) | safety provisions that comply with the requirements of the Network Service Provider must be incorporated into the substation facilities ; |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.4.8 |  | (b) | where required by the Network Service Provider , interfaces and accommodation must be provided by the User for metering, communication, remote monitoring and protection equipment to be installed in the substation by the Network Service Provider |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.4.8 |  | (c) | the substation must be capable of continuous uninterrupted operation within the system performance standards specified in section 2.2; |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.4.8 |  | (d) | the transformer vector group must be agreed with the Network Service Provider. The vector group must be compatible with the power system at the connection point and preference be given to vector groups with a zero sequence opening between high voltage and low voltage windings. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.4.8 |  | (e) | earthing of primary equipment in the substation must be in accordance with AS/NZS 3000:2000, and Western Australian Electrical Requirements . The earthing system must satisfy these requirements without any reliance on the Network Service Provider's equipment ; |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.4.8 |  | (f) | synchronisation facilities or reclose blocking must be provided if generating units are connected through the substation ; |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.4.8 |  | (g) | insulation levels of equipment in the substation must coordinate with the insulation levels of the transmission and distribution system to which the substation is connected without degrading the design performance of the transmission and distribution system . |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.4.9 |  | Load Shedding Facilities | Consumers must provide automatic load shedding facilities where required by the Network Service Provider in accordance with clause 2.3.1(c). |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.4.9.1 |  | Installation and Testing of Load Shedding Facilities | A Consumer that controls a load subject to load shedding in accordance with clause 2.3.1(c) must: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.4.9.1 |  | (a) | provide, install, operate and maintain equipment for load shedding ; |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.4.9.1 |  | (b) | co-operate with the Network Service Provider in conducting periodic functional testing of the load shedding equipment , which must not require load to be disconnected ; |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.4.9.1 |  | (c) | apply under frequency settings to relays as determined by the Network Service Provider ; and |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.4.9.1 |  | (d) | apply under-voltage settings to relays as determined by the Network Service Provider. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.4.10 |  | Monitoring and Control Requirements |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.4.10.1 |  | Remote Monitoring |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.4.10.1 |  | (a) | The Network Service Provider may require large transmission and distribution connected Users to: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | (a) (1) | provide remote monitoring equipment to enable System Management or the Network Service Provider to monitor the status and indications of the load remotely where this is necessary in real time for management, control, planning or security of the power system; and |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | (a) (2) | upgrade, modify or replace any RME already installed in a User's substation where the existing RME is, in the opinion of the Network Service Provider , no longer fit for purpose and notice is given in writing to the relevant Consumer . |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.4.10.1 |  | (b) | An RME provided, upgraded, modified or replaced (as applicable) in accordance with clause 3.4.10.1(a) must conform to an acceptable standard as agreed by the Network Service Provider and must be compatible with the Network Service Provider's SCADA system , including the requirements of clause 5.11. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.4.10.1 |  | (c) | Input information to RME may include the following: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | (c) (1) | status indications |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | (A) relevant circuit breakers open/closed (dual point) within the equipment ; |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | (B) relevant isolators within the equipment ; |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | (C) connection to the transmission or distribution system ; and |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | (D) relevant earth switches; |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | (c) (2) | alarms |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | (A) protection operation; |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | (B) protection fail; |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | (C) battery fail -AC and DC; |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | (D) trip circuit supervision; and |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | (E) trip supply supervision ; |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | (c) (3) | measured values |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | (A) active power load ; |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | (B) reactive power load ; |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | (C) load current; and |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | (D) relevant voltages throughout the equipment , including voltage on the Network Service Provider side of main switch. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.4.10.2 |  | Network Service Provider's Communications Equipment |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | Where remote monitoring equipment is installed in accordance with clause the User must provide communications paths (with appropriate redundancy) between the remote monitoring equipment and a communications interface in a location reasonably acceptable to the Network Service Provider . Communications systems between this communications interface and the relevant control centre are the responsibility of the Network Service Provider unless otherwise agreed. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.4.11 |  | Secure Electricity Supplies |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | All Users must provide secure electricity supplies of adequate capacity to provide for the operation for at least 8 hours of equipment performing metering, communication, monitoring, and protection functions, on loss of AC supplies. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.5 |  |  | USER’S PROTECTION REQUIREMENTS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.5.1 |  | Overview |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.5.1 |  | (a) | The requirements of this clause 3.5 apply only to a User's protection system that is necessary to maintain power system security. Protection systems installed solely to cover risks associated with a User's equipment are at the User's discretion. The extent of a User's equipment that will need to conform to the requirements of this clause 3.5 will vary from installation to installation. Consequently, each installation will need to be assessed individually by the Network Service Provider . Information that may be required by the Network Service Provider in order to complete this assessment is specified in Attachment 5. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.5.1 |  | (b) | The requirement for protection systems in respect of any User's equipment that forms an integral part of the transmission or distribution system (as seen from the transmission or distribution system ) is the same as would apply under clause 2.9 if that equipment were the Network Service Provider's equipment . For the purposes of this clause 3.5.1(b) a User’s equipment forms an integral part of the transmission and distribution system when the connection asset (such as a circuit breaker) that is used to disconnect a User’s equipment from the transmission or distribution system is owned by a User. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.5.1 |  | (c) | All Users’ equipment connected to the transmission or distribution system must be protected by protection systems or devices that automatically disconnect any faulty circuit from the transmission or distribution system . |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.5.1 |  | (d) | A User and the Network Service Provider must cooperate in the design and implementation of protection systems , including with regard to: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | (d) (1) | the use of current transformer and voltage transformer secondary circuits (or equivalent) of one party by the protection system of the other; |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | (d) (2) | tripping of one party's circuit breakers by a protection system of the other party; and |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | (d) (3) | (3) co-ordination of protection system settings to ensure interoperation. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Comment | Any reliance on the Network Service Provider's protection system to protect an item of User's equipment, and vice versa, including the use of current transformers and voltage transformers (or equivalent) and the tripping of circuit breakers, must be included in the relevant connection agreement. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.5.1 |  | (e) | A User's protection systems must be located on the relevant User's equipment and must discriminate with the Network Service Provider’s protection systems and that of other Users. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.5.1 |  | (f) | Except in an emergency, a User with equipment connected directly to the transmission system must notify the Network Service Provider at least 5 business day s prior to taking out of service all or part of a protection system of any equipment operating at a nominal voltage of 66 kV or greater. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.5.1 |  | (g) | The installation and use of automatic reclose equipment in a Consumer's facility is permitted only with the prior written agreement of the Network Service Provider . |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.5.1 |  | (h) | A Consumer must not adjust its protection settings without the Network Service Provider's approval. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.5.2 | Specific Protection Requirements for Generator Facilities |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | The requirements of this clause 3.5.2 do not apply to a generation facility |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.5.2 | (a) |  | where the total rating of all generating units in that generating facility is less than 10 MW and which are connected to the distribution system at a nominal voltage below 66 kV. For that case, the protection system requirements are specified in clauses 3.6 and 3.7. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.5.2 | (b) |  | The protection system for a generating unit must be designed to protect the generating unit from faults on the transmission or distribution system and to minimise damage to the generating unit from infeeds from the transmission and distribution system in the event of an internal fault. The main protection system must incorporate two fully independent protection schemes of differing principle , each discriminating with the transmission and distribution system . Where a critical fault clearance time exists, each protection scheme must be capable of operating to achieve the critical fault clearance time . Where there is no critical fault clearance time both independent protection schemes must meet the relevant maximum total fault clearance times specified in clause 2.9.4. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.5.2 | (c) |  | The design of the two fully independent protection schemes of differing principle must make it possible to test and maintain either protection scheme without interfering with the other. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.5.2 | (d) |  | The Generator's protection system and other controls must achieve the following functions: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | (d) (1) |  | disconnection of the Generator's generation from the transmission and distribution systems if any of the protection schemes required by clause 3.5.2(b) operate; |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | (d) (2) |  | separation of the Generator's generating unit from the transmission and distribution systems if there is a loss of supply to the User's installation from the transmission and distribution systems ; |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | (d) (3) |  | prevention of the Generator's generating unit from energising de-energised Network Service Provider equipment , or energising and supplying an otherwise isolated portion of the transmission or distribution system except where a Generator is contracted under the Wholesale Electricity Market Rules to provide a black start ancillary service and is directed to provide this service by System Management; |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | (d) (4) |  | adequate protection of the Generator's equipment without reliance on back up from the Network Service Provider's protection apparatus except as agreed with the Network Service Provider in accordance with clause 3.3.3.10 or 3.5.1(d); |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | (d) (5) |  | detection of a failure of a Generator's circuit breaker to clear a fault due to either mechanical or electrical failure. If such a failure is detected, the Generator User's protection system must send a trip signal to an alternative circuit breaker, which may be provided by the Network Service Provider in accordance with clause 3.5.1(d), in order to clear the fault. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.5.2 | (e) |  | A Generator must install check synchronising interlocks on all of its circuit breakers that are capable of out-of-synchronism closure, unless otherwise interlocked to the satisfaction of the Network Service Provider . |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.5.2 | (f) |  | If a generating unit is connected to the distribution system the Generator must provide a circuit breaker close inhibit interlock with the feeder circuit breaker at the Network Service Provider’s zone substation in accordance with the requirements specified by the Network Service Provider. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Comment: |  | [This interlock is required in addition to the islanding protection specified in clause 3.5.2(d)(3) on account of the potential safety hazard if a de-energised distribution feeder was energised by an embedded generating unit.] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.5.3 | Specific Protection Requirements for Consumer Facilities |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.5.3 | (a) |  | A Consumer must provide a main protection system to disconnect from the power system any faulted element within its protection zone within the total fault clearance time agreed with the Network Service Provider and specified in the relevant connection agreement . For equipment supplied from connection points with a nominal voltage of 33 kV or greater, the total fault clearance times are the relevant times specified in clause 2.9.4 unless a critical fault clearance time applies in accordance with clause 2.9.5, in which case the required total fault clearance time is the critical fault clearance time. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.5.3 | (b) |  | If the Consumer's connection point has a nominal voltage of 66 kV or greater, the main protection system must: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | (b) (1) |  | have sufficient redundancy to ensure that a faulted element is disconnected from the power system within the applicable fault clearance time as determined in accordance with clause 3.5.3(a) with any single protection element (including any communications facility upon which the protection system depends) out of service; |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | (b) (2) |  | provide a circuit breaker failure protection scheme to clear faults that are not cleared by the circuit breakers controlled by the primary protection system within the applicable fault clearance time as determined in accordance with clause 3.5.3(a). If a circuit breaker fails, the Consumer 's protection system may send a trip signal to a circuit breaker provided by the Network Service Provider in accordance with clause 3.5.1(d), in order to clear the fault. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.6 |  |  | REQUIREMENTS FOR CONNECTION OF SMALL GENERATING UNITS TO THE DISTRIBUTION NETWORK |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.6.1 | Overview |  | This clause 3.6 addresses the particular requirements for the connection of small generating units and groups of small generating units of aggregate rated capacity up to10 MW (small power stations) to the distribution system where such generating units are not subject to dispatch by System Management in accordance with the Market Rules. This does not apply to the connection of energy systems rated at up to 30 kVA and connected to the low voltage system via inverters, in respect of which clause 3.7 applies. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.6.2 | Categorisation of Facilities |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.6.2 | (a) |  | This clause 3.6 covers generating units of all types, whether using renewable or non-renewable energy sources. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.6.2 | (b) |  | Unless otherwise specified, technical requirements for generating units will apply at the connection point, rather than at the generator machine terminals, except that the reactive power requirements for synchronous generating units will apply at the generator machine terminals. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.6.2 | (c) |  | In this clause 3.6, connection points for small power stations are characterised as: (1) high voltage connected: 3 phase, 6.6 kV, 11 kV, 22 kV or 33 kV; or (2) low voltage connected: 1, 2 or 3 phase plus neutral, 240V or 415V. (3) Where a small power station is the only facility connected to a low voltage network the Generator may choose to have the power station assessed for compliance as if the power station was high voltage connected. Prior to another User subsequently connecting to the same low voltage network the Network Service Provider must reassess the power station for compliance with the requirements for low voltage connected power stations and the Generator must rectify any noncompliance identified in the reassessment. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.6.2 | (d) |  | Modes of Operation In this clause 3.6, the mode of operation of a generating unit in a small power station is characterised as: (1) being in continuous parallel operation with the distribution system, and either exporting electricity to the distribution system or not exporting electricity to it; (2) being in occasional parallel operation with the distribution system, and either exporting electricity to the distribution system or not exporting electricity to it, including generating units participating in peak lopping and system peak load management for up to 200 hours per year; (3) being in short term test parallel operation with the distribution system, and either exporting electricity to the distribution system or not exporting electricity to it, and having a maximum duration of parallel operation 2 hours per event and 24 hours per year; or (4) bumpless (make before break) transfer operation, being: (A) operation in rapid transfer mode where, when load is transferred between the generating unit and the distribution system or vice versa, the generating unit is synchronised for a maximum of one second per event; or (B) operation in gradual transfer mode where, when load is transferred between the generating unit and the distribution system or vice versa, the generating unit is synchronised for a maximum of 60 seconds per event. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.6.3 | Information Provided by the Generator |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.6.3 | (a) |  | A Generator must provide to the Network Service Provider information in relation to the design, construction, operation and configuration of that small power station as is reasonably required to ensure that the operation and performance standards of the distribution system, or other Users, are not adversely affected by the operation of the power station. Details of the kinds of information that may be required are included in Attachment 10. Where considered necessary by the Network Service Provider additional information of the kind included in Attachment 3 may be required |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.6.3 | (b) |  | In order to assess the impact of the equipment on the operation and performance of the distribution system or on other Users, the Network Service Provider may require a Generator to provide data on: (1) power station and generating unit aggregate real and reactive power; and (2) flicker coefficients and harmonic profile of the equipment, where applicable and especially for wind power and inverter connected equipment. Data on power quality characteristics, including flicker and harmonics, in accordance with IEC 61400-21 must be provided for all wind turbines. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.6.3 | (c) |  | Net import / export data must be provided in the form of: (1) a typical 24 hour power curve measured at 15 minute intervals (or better if available); and (2) details of the maximum kVA output over a 60 second interval, or such other form as specified in the relevant connection agreement. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.6.3 | (d) |  | When requested by the Network Service Provider, a Generator must provide details of the proposed operation of the equipment during start-up, shut-down, normal daily operation, intermittent fuel or wind variations and under fault or emergency conditions. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.6.3 | (e) |  | For generating units in a small power station of aggregate rating 5 MW and above, the Network Service Provider must assess the need for dynamic simulation studies and may require the Generator to provide a computer model in accordance with the requirements of clause 3.3.9. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.6.4 | Safety and Reliability |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.6.4 | (a) |  | The requirements imposed on a Generator by this clause 3.6 are intended to provide minimum safety and reliability standards for the distribution system and other Users. Subject to meeting these requirements, a Generator must design its facilities in accordance with applicable standards and regulations, good electricity industry practice and the manufacturers’ recommendations. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.6.4 | (b) |  | The safety and reliability of the distribution system and the equipment of other Users are paramount and access applications must be evaluated accordingly. Generators must not connect or reconnect to the distribution system if the safety and reliability of the distribution system would be placed at risk. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.6.4 | (c) |  | Where it is apparent that the operation of equipment installed in accordance with the requirements of this clause 3.6 may nevertheless have an adverse impact on the operation, safety or performance of the distribution system, or on the quality of supply to other Users, the Network Service Provider must consult with the User to reach an agreement on an acceptable solution. As a consequence, the Network Service Provider may require the Generator to test or modify its relevant equipment. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.6.4 | (d) |  | Unless otherwise agreed in the relevant connection agreement, the Network Service Provider may require a Generator not to operate equipment in abnormal distribution system operating conditions. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.6.4 | (e) |  | Equipment directly connected to the connection point of a small power station must be rated for the maximum fault current at the connection point specified in clause 2.5.8(b). |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.6.4 | (f) |  | A Generator must ensure that the maximum fault current contribution from a generating unit or small power station is not of a magnitude that will allow the total fault current at the connection point to exceed the levels specified in clause 2.5.8(b) for all distribution system operating conditions. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.6.5 | Applicable Requirements of clause 3.3 |  | Table 3.4 lists specific provisions of clause 3.3 that apply to small power stations in addition to the requirements of this clause 3.6. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 3.3.3.1 |  | Reactive power capability |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 3.3.3.3 |  | Generating unit response to disturbances Except that power stations with less than 150 kVA aggregate capacity need not comply with subclauses 3.3.3.3(c) and 3.3.3.3(g) unless directed otherwise by the Network Service Provider. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 3.3.3.8 |  | Protection of generating units from power system disturbances |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 3.3.4.4 |  | Frequency control systems Except that non-dispatchable induction generating units need not comply with subclauses (a), (b), (d) and (e)(2) and f(2); and Except that non-synchronous power stations with less than 150 kVA aggregate capacity do not have to comply with subclauses (a), (b) and (d). |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 3.3.4.5 |  | Voltage control systems Except that non-synchronous generating units may be fitted with power factor control systems utilising modern technology, unless power system studies show that fast acting voltage and / or reactive power control systems complying with clause 3.3.4.5(c) are required. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.6.6 | Generating Unit Characteristics |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.6.6 | (a) |  | To assist in controlling distribution system fault levels, Generators must ensure that generating units comply with the Network Service Provider’s requirements relating to minimum fault current and maximum fault current contribution through a connection point. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.6.6 | (b) |  | If the connection or disconnection of a User's small power station causes or is likely to cause excessively high or low fault levels, this must be addressed by other technical measures specified in the relevant connection agreement. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.6.7 | Connection and operation |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.6.7.1 | Generator’s Substations |  | Generators' substations through which generating units are connected to the distribution system must comply with the requirements of clause 3.4.8. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.6.7.2 | Main Switch |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.6.7.2 | (a) |  | Each facility at which a generating unit in a small power station is connected to the distribution system must contain one main switch provided by the User for each connection point and one main switch for each generating unit, where a generating unit shares a connection point with other generating units or loads. For larger installations, additional connection points and main switches or a dedicated feeder may be required. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.6.7.2 | (b) |  | Switches must be automatically operated, fault current breaking and making, ganged switches or circuit breakers. The relevant facility may also contain similarly rated interposed paralleling switches for the purpose of providing alternative synchronised switching operations. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.6.7.2 | (c) |  | At each relevant connection point there must be a means of visible and lockable isolation and test points accessible to the Network Service Provider's operational personnel. This may be a withdrawable switch, a switch with visible contacts, a set of removable links or other approved means. It must be possible for the Network Service Provider’s operational personnel to fit safety locks on the isolation point. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.6.7.3 | Synchronising |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.6.7.3 | (a) |  | For a synchronous generating unit in a small power station, a Generator must provide automatic synchronising equipment at each generating unit circuit breaker. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.6.7.3 | (b) |  | Check synchronising must be provided on all generating unit circuit breakers and any other switching devices that are capable of connecting the User's generating equipment to the distribution system unless otherwise interlocked to the satisfaction of the Network Service Provider. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.6.7.3 | (c) |  | Prior to the initial synchronisation of the generating unit(s) to the distribution system, the Generator and the Network Service Provider must agree on written operational procedures for synchronisation. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.6.7.4 | Safe Shutdown without external Supply |  | A generating unit must be capable of being safely shut down without electricity supply being available from the distribution system. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.6.8 | Power Quality and Voltage Change |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.6.8 | (a) |  | A Generator must ensure that the performance standards of clause 2.2 are met when a small power station is connected by it to the distribution system. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.6.8 | (b) |  | The step voltage change at the connection point for connection and disconnection must comply with the requirements of clause 2.2.2. On low voltage feeders, voltage changes up to 5% may be allowed in some circumstances with the approval of the Network Service Provider. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.6.8 | (c) |  | The steady state voltage rise at the connection point resulting from export of power to the distribution system must not cause the voltage limits specified in clause 2.2 to be exceeded and, unless otherwise agreed with the Network Service Provider, must not exceed 2%. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.6.8 | (d) |  | When operating unsynchronised, a synchronous generating unit in a small power station must generate a constant voltage level with balanced phase voltages and harmonic voltage distortion equal to or less than permitted in accordance with either Australian Standard AS 1359 (1997) "General Requirements for Rotating Electrical Machines" or a recognised relevant international standard, as agreed between the Network Service Provider and the User. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.6.9 | Remote Control, Monitoring and Communication |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.6.9 | (a) |  | For generating units exporting 1 MVA or more to the distribution system the Generator must provide for: (1) tripping of the generating unit remotely from the Network Service Provider’s control centre; (2) a close-enable interlock operated from the Network Service Provider’s control centre; and (3) remote monitoring at the control centre of (signed) MW, MVAr and voltage. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.6.9 | (b) |  | For generating units exporting less than 1 MVA monitoring may not be required. However, where concerns for safety and reliability arise that are not adequately addressed by automatic protection systems and interlocks, the Network Services Provider may require the Generator to provide remote monitoring and remote control of some functions in accordance with clause 3.6.9(a). |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.6.9 | (c) |  | A Generator must provide a continuous communication link with the Network Service Provider’s control centre for monitoring and control for generating units exporting 1 MVA and above to the distribution system. For generating units exporting below 1 MVA, non-continuous monitoring and control may be required e.g. a bi-directional dial up arrangement. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.6.9 | (d) |  | A Generator must have available at all times a telephone link or other communication channel to enable voice communications between a small power station and the Network Service Provider's control centre. For generating units exporting above 1 MVA, a back-up speech communication channel pursuant to clause 3.3.4.3(d) may be required. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.6.10 | Protection |  | This clause 3.6.10 applies only to protection necessary to maintain power system security. A Generator must design and specify any additional protection required to guard against risks within the Generator's facility. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.6.10.1 | General |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.6.10.1 | (a) |  | A Generator must provide, as a minimum, the protection functions specified in this clause 3.6.10 in accordance with the aggregate rated capacity of generating units in a small power station at the connection point. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.6.10.1 | (b) |  | A Generator's proposed protection system and settings must be approved by the Network Service Provider, who must assess their likely effect on the distribution system and may specify modified or additional requirements to ensure that the performance standards specified in clause 2.2 are met, the power transfer capability of the distribution system is not reduced and the quality of supply to other Users is maintained. Information that may be required by the Network Service Provider prior to giving approval is specified in Attachment 5 and Attachment 10. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.6.10.1 | (c) |  | A Generator’s protection system must clear internal plant faults and coordinate with the Network Service Provider’s protection system. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.6.10.1 | (d) |  | The design of a Generator's protection system must ensure that failure of any protection device cannot result in the distribution system being placed in an unsafe operating mode or lead to a disturbance or safety risk to the Network Service Provider or to other Users. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.6.10.1 | (e) |  | All protection apparatus must comply with the IEC 60255 series of standards. Integrated control and protection apparatus may be used provided that it can be demonstrated that the protection functions are functionally independent of the control functions, i.e. failure or mal-operation of the control features will not impair operation of the protection system. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.6.10.1 | (f) |  | All small power stations must provide under and over voltage, under and over frequency and overcurrent protection schemes in accordance with the equipment rating. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.6.10.1 | (g) |  | All small power stations must provide earth fault protection for earth faults on the distribution system. All small power stations connected at high voltage must have a sensitive earth fault protection scheme. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.6.10.1 | (h) |  | All small power stations must provide protection against abnormal distribution system conditions, as specified in clause 3.3.3.8, on one or more phases. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.6.10.1 | (i) |  | All small power stations that have an export limit shall have directional (export) power or directional current limits set appropriate to the export limit. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.6.10.1 | (j) |  | All small power stations must have loss of AC and DC auxiliary supply protection, which must immediately trip all switches that depend on that supply for operation of their protection, except where the auxiliary supply is duplicated in which case the failure may be alarmed in accordance with clause 3.6.12. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.6.10.1 | (k) |  | Where synchronisation is time limited, the small power station must be disconnected by an independent timer |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.6.10.1 | (l) |  | Generating units that are only operated in parallel with the distribution system during rapid bumpless transfer must be protected by an independent timer that will disconnect the generating unit from the distribution system if the bumpless transfer is not successfully completed. Automatic transfer switches must comply with AS 60947.6.2 (2004). For the avoidance of doubt generating units covered by this clause need not comply with subclauses (f) to (k) of this clause 3.6.10.1. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.6.10.2 | Pole Slipping |  | Where it is determined that the disturbance resulting from loss of synchronism is likely to exceed that permitted in clause 2.2, the Generator must install a pole slipping protection scheme. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.6.10.3 | Islanding Protection |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.6.10.3 | (a) |  | No small power station may supply power into any part of the distribution system that is disconnected from the power system |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.6.10.3 | (b) |  | For parallel operation (which excludes rapid or gradual bumpless transfer), islanding protection schemes of two different functional types must be provided to prevent a generating unit energising a part of the distribution system that has become isolated from the remainder of the transmission or distribution system under all operating modes. The Generator must demonstrate that two different functional types of islanding protection schemes have been provided |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.6.10.3 | (c) |  | For power stations rated above 1 MVA, each functional type of islanding protection scheme must be incorporated into a physically separate protection relay. These may share the same voltage and current transformers but must be connected to different secondary windings. This requirement may be applied to power stations rated below 1 MVA in situations where it is possible for the power station to support a sustained island on a part of the high voltage distribution system. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.6.10.3 | (d) |  | Except as provided in clause 3.6.10.3(c) where a power station is rated at less than 1 MVA the two islanding protection schemes may be incorporated into the same multi-function protection relay, provided that the overcurrent and earth fault protection schemes required by clauses 3.6.10.1(f) and 3.6.10.1(g) are in a physically separate relay. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.6.10.3 | (e) |  | Where there is no export of power into the distribution system and the aggregate rating of the power station is less than 150kVA, islanding protection schemes can be in the form of a directional power function that will operate for power export. Directional overcurrent relays may also be used for this purpose. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.6.10.3 | (f) |  | Generating units designed for gradual bumpless transfer must be protected with at least one functional type of loss of mains protection scheme. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.6.10.3 | (g) |  | Islanding protection must operate within 2 seconds to ensure disconnection before the first distribution system reclosing attempt (typically 5 seconds). Relay settings are to be agreed with the Network Service Provider. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.6.11 | Intertripping |  | In cases where, in the opinion of the Network Service Provider, the risk of undetected islanding of part of the distribution system and the Generator's facility remains significant, the Network Service Provider may also require the installation of an intertripping link between the Generator's main switch(es) and the feeder circuit breaker(s) in the zone substation or other upstream protection device nominated by the Network Service Provider. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.6.12 | Failure of Generator’s Equipment |  | Any failure of the Generator's protection apparatus must automatically trip the generating unit’s main switch except, where the affected protection apparatus forms part of a protection system comprised of two fully independent protection schemes of differing principle, the failure may instead be alarmed within the Generator’s facility provided that operating procedures are in place to ensure that prompt action is taken to remedy such failures. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.6.13 | Commissioning and Testing |  | The Generator must comply with the testing and commissioning requirements for generating units connected to the distribution system specified in Attachment 12. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.6.14 | Technical Matters to be Coordinated |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.6.14 | (a) |  | The Generator and the Network Service Provider must agree upon the following matters in respect of each new or altered connection: (1) design at connection point; (2) physical layout adjacent to connection point; (3) back-up (alternative) supply arrangements; (4) protection and back-up; (5) control characteristics; (6) communications, metered quantities and alarms; (7) insulation co-ordination and lightning protection; (8) fault levels and fault clearing times; (9) switching and isolation facilities; (10) interlocking arrangements; (11) synchronising facilities; (12) under frequency load shedding and islanding schemes; and (13) any special test requirements. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.6.14 | (b) |  | As an alternative to distribution system augmentation, the Network Service Provider may require a Generator to provide additional protection schemes to ensure that operating limits and agreed import and export limits are not exceeded. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.7 |  |  | Not applicable for this TCR version |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 4.1 |  |  | COMMISSIONING OF USER’S EQUIPMENT |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 4.1 / 4.1.1. | Inspection and testing |  | t.b.a. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 4.1.2 | Right of testing |  | t.b.a. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 4.1.3 | Tests to demonstrate compliance with connection requirements for Generators |  |  |  |  | Note: This TCR report assists in meeting this requirement |  |  |  |  |  |  |  |  |  |  |  |
|  | (a) (b) (c) (d) (e) (f) (g) (h) |  | A Generator must provide evidence to the Network Service Provider that each of its generating units complies with the technical requirements of clause 3.3, or 3.6, as applicable, and the relevant connection agreement prior to commencing commercial operation. In addition, each Generator must cooperate with the Network Service Provider and, if necessary, System Management in carrying out power system tests prior to commercial operation in order to verify the performance of each generating unit, and provide information and data necessary for computer model validation. The test requirements for synchronous generating units are detailed in Table A11.1 of Attachment 11. The Network Service Provider must specify test requirements for non-synchronous generation. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 4.1.4 | Routine Testing of Protection Equipment |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 4.1.5 | Testing by Users of their own equipment requiring changes to agreed operation |  | t.b.a. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 4.1.6 | Tests for changes |  | t.b.a |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 4.1.7 | Power system tests |  | t.b.a |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 4.2 |  |  | COMMISSIONING OF USER’S EQUIPMENT |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 4.2.1 |  |  | Requirement to Inspect and Test Equipment |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | (a) |  | A User must ensure that new or replacement equipment is inspected and tested to demonstrate that it complies with relevant Australian Standards, relevant international standards, these Rules, the Access Code and any relevant connection agreement and good electricity industry practice prior to being connected to a transmission or distribution system. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | (b) |  | If a User installs or replaces equipment at a connection point, the Network Service Provider is entitled to witness the inspections and tests described in clause 4.1.1(a). |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 4.2.2 | (a) |  | A User seeking to connect equipment to a transmission or distribution system must cooperate with the Network Service Provider to develop procedures to ensure that the commissioning of the connection and connected facility is carried out in a manner that: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | (1) |  | does not adversely affect other Users or affect power system security or quality of supply of the power system; and |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | (2) |  | minimises the threat of damage to the Network Service Provider's or any other User's equipment. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | (b) |  | A User may request from the Network Service Provider to schedule commissioning and tests (including the relevant exchange of correspondence) at particular times that suit the project completion dates. The Network Service Provider must make all reasonable efforts to accommodate such a request. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | (c) |  | A User must not connect equipment to the network without the approval of the Network Service Provider who must not approve such connection before the User’s installation has been certified for compliance with these Rules and the WA Electrical Requirements. To avoid doubt, clause 4.2.2(c) does not apply if clause 3.7 applies. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 4.2.3 | Control and Protection Settings for Equipment |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | (a) |  | Not less than 65 business days (or as otherwise agreed between the User and the Network Service Provider) prior to the proposed commencement of commissioning by a User of any new or replacement equipment that could reasonably be expected to alter materially the performance of the power system, the User must submit to the Network Service Provider sufficient design information including proposed parameter settings to allow critical assessment including analytical modelling of the effect of the new or replacement equipment on the performance of the power system. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | (b) |  | The Network Service Provider must: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | (1) |  | consult with other Users and System Management as appropriate; and |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | (2) |  | within 20 business days of receipt of the design information under clause 4.2.3(a), notify the User of any comments on the proposed parameter settings for the new or replacement equipment |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | (c) |  | If the Network Service Provider's comments include alternative parameter settings for the new or replacement equipment, then the User must notify the Network Service Provider within 10 business days that it either accepts or disagrees with the alternative parameter settings suggested by the Network Service Provider |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | (d) |  | The Network Service Provider and the User must negotiate parameter settings that are acceptable to them both and if there is any unresolved disagreement between them, the matter must be determined by means of the disputes procedure provided for in clause 1.7. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | (e) |  | The User and the Network Service Provider must co-operate with each other to ensure that adequate grading of protection is achieved so that faults within the User's facility are cleared without adverse effects on the power system. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 4.2.4 | Commissioning Program |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | (a) |  | Not less than 65 business days (or as otherwise agreed between the User and the Network Service Provider) prior to the proposed commencement of commissioning by a User of any new or replacement equipment that could reasonably be expected to alter materially the performance of the power system, the User must advise the Network Service Provider in writing of the commissioning program including test procedures and proposed test equipment to be used in the commissioning. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | (b) |  | The Network Service Provider must, within 20 business days of receipt of such advice under clause 4.2.4(a), notify the User either that it: (1) agrees with the proposed commissioning program and test procedures; or (2) requires changes in the interest of maintaining power system security, safety or quality of supply |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | (c) |  | If the Network Service Provider requires changes, then the Network Service Provider and the User must co-operate to reach agreement and finalise the commissioning program within a reasonable period. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | (d) |  | A User must not commence the commissioning until the commissioning program has been finalised and the Network Service Provider must not unreasonably delay finalising a commissioning program. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 4.2.5 | Commissioning Tests |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | (a) |  | The Network Service Provider and System Management have the right to witness commissioning tests relating to new or replacement equipment including remote monitoring equipment, protection and control and data acquisition equipment, that could reasonably be expected to alter materially the performance of the power system or the accurate metering of energy or be required for the real time operation of the power system |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | (b) |  | Prior to connection to the transmission or distribution system of new or replacement equipment covered by clause 4.2.5(a), a User must provide to the Network Service Provider a signed written statement to certify that the inspection and tests required under clause 4.2.1(a) have been completed and that the equipment is ready to be connected and energised. The statement must be certified by a Chartered Professional Engineer with National Professional Engineers’ Register Standing qualified in a relevant discipline. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | (c) |  | The Network Service Provider must, within a reasonable period of receiving advice of commissioning tests of a User's new or replacement equipment under this clause 4.2.5, advise the User whether or not it: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | (1) |  | wishes to witness the commissioning tests; and |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | (2) |  | agrees with the proposed commissioning times. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | (d) |  | A User whose new or replacement equipment is tested under this clause 4.2.5 must, as soon as practicable after the completion of the relevant tests, submit to the Network Service Provider the commissioning test results demonstrating that a new or replacement item of equipment complies with these Rules or the relevant connection agreement or both to the satisfaction of the Network Service Provider |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | (e) |  | If the commissioning tests conducted under this clause 4.2.5 in relation to a User's new or replacement item of equipment demonstrate non-compliance with one or more requirements of these Rules or the relevant connection agreement, then the User must promptly meet with the Network Service Provider to agree on a process aimed at achieving compliance with the relevant item in these Rules. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | (f) |  | The Network Service Provider may direct that the commissioning and subsequent connection of a User's equipment must not proceed if the relevant equipment does not meet the technical requirements specified in clause 4.2. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | (g) |  | All commissioning tests under this clause 4.2.5 must be carried out under the supervision of personnel experienced in the commissioning of power system primary equipment and secondary equipment. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 4.2.6 | Coordination of protection settings |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | (a) |  | A User must ensure that its protection settings coordinate with the existing protection settings of the transmission and distribution system. Where this is not possible, the User may propose revised protection settings, for the transmission and distribution system to the Network Services Provider. In extreme situations it may be necessary for a User to propose a commercial arrangement to the Network Service Provider to modify the transmission or distribution system protection. The Network Service Provider must consider all such proposals but it must not approve a User's protection system until protection coordination problems have been resolved. In some situations, the User may be required to revise the Network Service Provider settings or upgrade the Network Service Provider or other Users' equipment, or both. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | (b) |  | If a User seeks approval from the Network Service Provider to apply or change a control or protection system setting, this approval must not be withheld unless the Network Service Provider reasonably determines that the changed setting would cause the User not to comply with the requirements of clause 3 of these Rules, or the power system not to comply with the performance standards specified in clause 2.2, or the Network Service Provider or some other User not to comply with their own protection requirements specified in the respective clauses 2.9 and 3.5, or the power transfer capability of the transmission or distribution system to be reduced. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | (c) |  | If the Network Services Provider reasonably determines that a setting of a User's control system or protection system needs to change in order for the User to comply with the requirements of clause 3 of these Rules, or for the power system to meet the performance standards specified in clause 2.2, or so as not to cause the Network Service Provider or some other User to fail to comply with its own protection requirements specified in clause 2.9 or 3.5, as applicable, or for the power transfer capability of the transmission or distribution system to be restored, the Network Service Provider must consult with the User and may direct in writing that a setting be applied in accordance with the determination. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | (d) |  | The Network Service Provider may require a test in accordance with clause 4.1.3 to verify the performance of the User's equipment with any new setting. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 4.2.7 | Approval of Proposed Protection |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | (a) |  | A User must not allow its plant to take supply of electricity from the power system without prior approval of the Network Service Provider. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | (b) |  | A User must not change the approved protection design or settings without prior written approval of the Network Service Provider. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 5 | TRANSMISSION AND DISTIRBUTION SYSTEM OPERATION AND COORDINATION |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 5.1 – 5.3 |  |  | <<Insert additional rows as applicable…>> |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 5.3.3 | User Obligations |  | Procedures prepared and in place can address these obligations |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | (a) |  | A User must ensure that only appropriately qualified and competent persons operate equipment that is directly connected to the transmission or distribution system through a connection point. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | (b) |  | A User must co-operate with any review of operating incidents undertaken by the Network Service Provider or System Management under clause 5.7.3. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | (c) |  | A User must co-operate with and assist the Network Service Provider or System Management in the proper discharge of the transmission or distribution system operation and co-ordination responsibilities. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | (d) |  | A User must operate its facilities and equipment in accordance with any direction given by the Network Service Provider or System Management. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | (e) |  | A User must notify System Management or, where appropriate, the Network Service Provider, prior to a generating unit being operated in a mode (e.g. "turbine-follow" mode) where the generating unit will be unable to respond in accordance with clause 3.3.4.4. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | (f) |  | Except in an emergency, a User must notify the Network Service Provider at least 5 business days prior to taking a protection of transmission plant out of service. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | (g) |  | Except in an emergency, a User must notify the Network Service Provider at least 5 business days prior to taking a protection of distribution plant out of service if this protection is required to meet a critical fault clearance time. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | <<Insert additional rows as required…>> |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | ATTACHMENT 3 - SUMMARY OF SCHEDULES OF TECHNICAL DETAILS TO SUPPORT APPLICATION FOR CONNECTION |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | ATTACHMENT 5 - SUBMISSION REQUIREMENTS FOR ELECTRICAL PLANT PROTECTION |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Protection data submission timelines: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | S= Std planning data, D = Detailed planning data, R = Registered data (R1 pre-connection, R2 post-connection) |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | D |  | Within 3 months of signing of the connection agreement, or as agreed otherwise in the connection agreement. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | R1 |  | At least 3 months prior to commencement of protection equipment commissioning, or as agreed otherwise in the connection agreement. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | R2 |  | Within 3 weeks of the completion of protection equipment commissioning, or as agreed otherwise in the connection agreement. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Data Description Data Category |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Protection Design Philosophy: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | Documentation explaining the general protection philosophy, including: - Present and design minimum and maximum fault levels. - Present and design minimum and maximum fault contributions to the network from the User, at the connection point. - Details of required critical fault clearance times, and which protections will be employed to meet these times. - Local Backup (circuit breaker fail) philosophy. - Special scheme philosophy (for example, islanding or load shedding schemes). - Protection number 1 philosophy - Protection number 2 philosophy D, R1 and R |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | Power single line diagram, down to and including the low voltage (greater than 50V AC) bus(s), including: - Voltage levels, - Transformer ratings, winding configurations and earthing connections - Generator ratings and earthing connections - Operating status of switching devices - Earthing configuration D, R1 and R2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | - Primary plant interlocks Details of protection interfaces between the network and the User D, R1 and R2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | Protection single line diagram, down to and including the low voltage (greater than 50V AC) bus(s), including: - Current transformer locations, rated primary and secondary current, rated short-time thermal current, rated output, accuracy class and designation. - Voltage Transformer locations, winding connections, rated primary and secondary voltages, rated output and accuracy class. - Relay make and model number - Relay functions employed - Primary plant mechanical protections - Trip details (diagrammatic or by trip matrix) R1 and R2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | Impedance diagram of the system, showing, for each item of primary plant, details of the positive, negative and zero sequence series and shunt impedances, including mutual coupling between physically adjacent elements. Impedances to be in per unit, referred to a 100MVA base. Final submission (R2) to include tested values of generator and transformer impedances (for example, from manufacturer’s test certificates) R1 and R2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | Tripping and control power supply (e.g. DC system) single line diagram. R1 and R2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | Power flow details at point of connection as per the data requested in Attachment 5. R1 and R2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | HV circuit breaker details, including: - A control and protection schematic diagram of the circuit breaker(s) at the User connection to the network - Type, rated current and rated fault MVA or rated breaking current of all HV circuit breakers R1 and R2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | HV switch fuse details, including: - Rated current of fuse - Rated breaking current of fuse - Type of fuse - Current-time characteristic curves R1 and R2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Protection Settings Design Philosophy: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | Documentation explaining the general protection settings philosophy R1 and R2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | Calculated critical fault clearance times R1 and R2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | Protection function settings to be employed and reasons for selecting these settings. Diagrams to be submitted where applicable. R1 and R2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | Overcurrent grading curves for phase faults. R1 and R2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | Overcurrent grading curves for earth faults R1 and R2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | ATTACHMENT 7 - TRANSMISSION SYSTEM AND EQUIPMENT TECHNICAL DATA OF EQUIPMENT AT OR NEAR CONNECTION POINT |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | ATTACHMENT 8 - TRANSMISSION SYSTEM EQUIPMENT AND APPARATUS SETTING DATA |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | ATTACHMENT 9 - LOAD CHARACTERISTICS AT CONNECTION POINT |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | COPY AND INSERT OTHER ATTACHMENT SUPPORTING ROWS AS REQUIRED |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

# Certification

Name of Customer or Generator:

Authorised Representative:

Facility Name & Address:

CERTIFICATION

I,________________________________________________________________________________

(name of chartered professional engineer with NPER standing)

certify that the information provided throughout this document for the purposes of demonstrating full compliance with all relevant Technical Rules is both complete and accurate.

Signature:

(Signature of Registered Professional Engineer)

Date:

https://www.erawa.com.au/electricity/electricity-access/western-power-network/technical-rules

http://www.finance.wa.gov.au/cms/uploadedFiles/Public_Utilities_Office/Energy_Initiatives/Current_Electricity_Networks_Access_Code_2004.pdf

https://www.engineersaustralia.org.au/national-engineering-register

http://www.aemo.com.au/Electricity/Market-Operations/Generator-Performance-Standards